## General assumptions
General parametres
Parameter | Value
Discount Rate | 8%
Other (technology specific) parameters
Generation source | Micro Grid connected/ Stand Alone | Plant capacity (MW) | Operational life (Years) | Capacity factor (average) | Efficiency | source
Diesel gen (micro) | Stand Alone | <0.025 | 10 | 50% | 0.28 | [1], [3], IEA inputs
Diesel generator (mini) | Micro Grid connected | 0.1 | 15 | 70% | 0.33 | [1], [3], IEA inputs
Solar PV (mini) | Stand Alone | 0.0003 | 10 | Obtained for each grid point | - | [1], [3], IEA inputs
Solar PV (middle) | Micro Grid connected | 0.025 | 20 | Obtained for each grid point | - | [1], [3], IEA inputs
Wind onshore (mini) | Micro Grid connected | 0.1 | 20 | Obtained for each grid point | - | [1], [3], IEA inputs
Micro hydro | Micro Grid connected | 0.1 | 30 | 35% | - | [1], [3], IEA inputs

## Capital costs
Capital investment costs for year 1 of the model
| Generation source | Plant capacity (MW) | Year 1 capital investement cost (US$/kW) | Reference-Assumptions
| Diesel gen (micro) | 0.025 | 937.8457 | Starting from the price for mini DG (2010) indicated in [1] , with IEA projections
| Diesel generator (mini) | 0.1 | 721.4197 | Starting from the price for mini DG (2010) indicated in [1] , with IEA projections
| Solar PV (mini) | 0.0003 | 6000 | IEA - Given
| Solar PV (middle) | 0.025 | 5000 | IEA - Given
| Wind onshore (mini) | 0.1 | 3675 | IEA - Given
| PV-wind hybrid (mini) | 0.1 | 7893.2631 | IEA - Given
| Micro hydro | 0.1 | 5000 | IEA - Given
Capital investment costs projections for generation technologies suggested by IEA (US$/kW)
Cost reduction rate (%/yr) - Ref: IEA given | Generation source | Plant capacity (MW) | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
0% | Diesel gen (micro) | 0.025 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457 | 937.8457
0% | Diesel generator (mini) | 0.1 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197 | 721.4197
-2% | Solar PV (mini) | 0.0003 | 6367.248 | 6242.4 | 6120 | 6000 | 5880 | 5762.4 | 5647.152 | 5534.209 | 5423.5248 | 5315.0543 | 5208.7532 | 5104.5781 | 5002.4866 | 4902.4368 | 4804.3881 | 4708.3003 | 4614.1343 | 4521.8516 | 4431.4146 | 4342.7863 | 4255.9306
-2% | Solar PV (middle) | 0.025 | 5306.04 | 5202 | 5100 | 5000 | 4900 | 4802 | 4705.96 | 4611.8408 | 4519.604 | 4429.2119 | 4340.6277 | 4253.8151 | 4168.7388 | 4085.364 | 4003.6568 | 3923.5836 | 3845.1119 | 3768.2097 | 3692.8455 | 3618.9886 | 3546.6088
-0.6% | Wind onshore- between 100kw and 300kw | 0.1 | 3741.5477 | 3719.2323 | 3697.05 | 3675 | 3652.95 | 3631.0323 | 3609.2461 | 3587.5906 | 3566.0651 | 3544.6687 | 3523.4007 | 3502.2603 | 3481.2467 | 3460.3592 | 3439.5971 | 3418.9595 | 3398.4457 | 3378.0551 | 3357.7867 | 3337.64 | 3317.6142
-1.4% | PV-wind hybrid (mini) | 0.1 | 8229.4431 | 8115.8216 | 8003.7688 | 7893.2631 | 7782.7574 | 7673.7988 | 7566.3656 | 7460.4365 | 7355.9904 | 7253.0065 | 7151.4644 | 7051.3439 | 6952.6251 | 6855.2884 | 6759.3143 | 6664.6839 | 6571.3784 | 6479.3791 | 6388.6678 | 6299.2264 | 6211.0372
-0.3% | Micro hydro | 0.1 | 5045.1351 | 5030.045 | 5015 | 5000 | 4985 | 4970.045 | 4955.1349 | 4940.2695 | 4925.4487 | 4910.6723 | 4895.9403 | 4881.2525 | 4866.6087 | 4852.0089 | 4837.4529 | 4822.9405 | 4808.4717 | 4794.0463 | 4779.6641 | 4765.3251 | 4751.0292
Main assumptions (additional to the costs listed below):
The capital cost for the first year of the projection was calculated with the most reliable source for small scale technologies, and cheched with other sources as indicated bleow. Cost projections are selected according to the IEA NPS reccomendations.

## Fuel costs
Fuel costs for year 1 of the model - Nigeria | [5 empty] | Fuel costs for year 1 of the model - Ethiopia
| Source | Value | unit |  |  |  | Source | Value | unit
Diesel pump price in NIGERIA (2012) | [9] | 1.09 | $/l |  |  | Diesel pump price in NIGERIA (2012) | [9] | 0.94 | $/l
Year 1 fuel price for Stand Alone DG | As pump price | 0.109 | $/kWh |  |  | Year 1 fuel price for Stand Alone DG | As pump price | 0.094 | $/kWh
Year 1 fuel price for Micro-Grid connected DG | Pump price reduced by 30% | 0.0763 | $/kWh |  |  | Year 1 fuel price for Micro-Grid connected DG | Pump price reduced by 30% | 0.0658 | $/kWh
Grid Electricity cost Nigeria (2012) | [9] | 0.15 | $/kWh |  |  | Grid Electricity cost Nigeria (2012) | [9] | 0.15 | $/kWh
Projected fuel costs projections (US$/kWh) - NIGERIA
| Source |  | Unit | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Projected fuel price for Stand Alone DG* | IEA NPS recommendation | - | $/kWh | 0.109 | 0.109 | 0.109 | 0.109 | 0.10955 | 0.11009 | 0.11064 | 0.1112 | 0.11175 | 0.11231 | 0.11287 | 0.11344 | 0.114 | 0.11457 | 0.11515 | 0.11572 | 0.1163 | 0.11688 | 0.11747 | 0.11805 | 0.11865
projected fuel price for Micro-Grid connected DG* | IEA NPS recommendation | - | $/kWh | 0.0763 | 0.0763 | 0.0763 | 0.0763 | 0.076681 | 0.077065 | 0.07745 | 0.077837 | 0.078227 | 0.078618 | 0.079011 | 0.079406 | 0.079803 | 0.080202 | 0.080603 | 0.081006 | 0.081411 | 0.081818 | 0.082227 | 0.082638 | 0.083052
Projected Grid Elecrtcity price | IEA NPS recommendation | - | $/kWh | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.14925 | 0.1485 | 0.14776 | 0.14702 | 0.14629 | 0.14556 | 0.14483 | 0.1441 | 0.14338 | 0.14267 | 0.14195 | 0.14124 | 0.14054 | 0.13983 | 0.13914 | 0.13844
[7 empty] | 76.3 | 76.6815 | 77.0649 | 77.4502 | 77.8375 | 78.2267 | 78.6178 | 79.0109 | 79.4059 | 79.803 | 80.202 | 80.603 | 81.006 | 81.411 | 81.8181 | 82.2272 | 82.6383 | 83.0515
Projected fuel costs projections (US$/kWh) - Ethiopia
| Source |  | Unit | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Projected fuel price for Stand Alone DG* | IEA NPS recommendation | - | $/kWh | 0.094 | 0.094 | 0.094 | 0.094 | 0.09447 | 0.094942 | 0.095417 | 0.095894 | 0.096374 | 0.096855 | 0.09734 | 0.097826 | 0.098316 | 0.098807 | 0.099301 | 0.099798 | 0.1003 | 0.1008 | 0.1013 | 0.10181 | 0.10232
projected fuel price for Micro-Grid connected DG* | IEA NPS recommendation | - | $/kWh | 0.0658 | 0.0658 | 0.0658 | 0.0658 | 0.066129 | 0.06646 | 0.066792 | 0.067126 | 0.067462 | 0.067799 | 0.068138 | 0.068479 | 0.068821 | 0.069165 | 0.069511 | 0.069858 | 0.070208 | 0.070559 | 0.070912 | 0.071266 | 0.071622
Projected Grid Elecrtcity price | IEA NPS recommendation | - | $/kWh | - | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
[7 empty] | 65.8 | 66.129 | 66.4596 | 66.7919 | 67.1259 | 67.4615 | 67.7988 | 68.1378 | 68.4785 | 68.8209 | 69.165 | 69.5108 | 69.8584 | 70.2077 | 70.5587 | 70.9115 | 71.2661 | 71.6224
Main assumptions (additional to the costs listed below):
*Note for Diesel fuel costs: Starting from the costs listed below, for each grid cell in the map the cost is recalculated inclluding as well the costs associated to de need of fuel transportation from the closest diesel refournishment, according to the methodology described in [11]
*For stand alone DG fuel price for Y1 model assumed as the average Diesel price at the pump station in Nigeria, found on the WB indicators databas. For Micro-grid connected DG this price is reduced by 30%. Cost projections are selected according to the IEA NPS reccomendations

## O&M costs
O&M costst costs for generation technologies (US$/year/kW)
Generation source | Plant capacity (MW) | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Diesel gen (micro) | 0.025 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846 | 93.7846
Diesel generator (mini) | 0.1 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142 | 72.142
Solar PV (mini) | 0.0003 | 127.345 | 124.848 | 122.4 | 120 | 117.6 | 115.248 | 112.943 | 110.6842 | 108.4705 | 106.3011 | 104.1751 | 102.0916 | 100.0497 | 98.0487 | 96.0878 | 94.166 | 92.2827 | 90.437 | 88.6283 | 86.8557 | 85.1186
Solar PV (middle) | 0.025 | 106.1208 | 104.04 | 102 | 100 | 98 | 96.04 | 94.1192 | 92.2368 | 90.3921 | 88.5842 | 86.8126 | 85.0763 | 83.3748 | 81.7073 | 80.0731 | 78.4717 | 76.9022 | 75.3642 | 73.8569 | 72.3798 | 70.9322
Wind onshore- between 100kw and 300kw | 0.1 | 74.831 | 74.3846 | 73.941 | 73.5 | 73.059 | 72.6206 | 72.1849 | 71.7518 | 71.3213 | 70.8934 | 70.468 | 70.0452 | 69.6249 | 69.2072 | 68.7919 | 68.3792 | 67.9689 | 67.5611 | 67.1557 | 66.7528 | 66.3523
Micro hydro | 0.1 | 164.5889 | 162.3164 | 160.0754 | 157.8653 | 155.6551 | 153.476 | 151.3273 | 149.2087 | 147.1198 | 145.0601 | 143.0293 | 141.0269 | 139.0525 | 137.1058 | 135.1863 | 133.2937 | 131.4276 | 129.5876 | 127.7734 | 125.9845 | 124.2207
Main assumptions (additional to the costs listed below):
O&M cost are taken, as default value, and comparing a number of studies from i.e. (ESMAP,Columbia…etc), at 2% of the capitali investment/year for renewable energy technology, and 10% of the capital investment/year for Diesel generators.

## T&D costs & assumptions
Transmission & Distribution costs
Parameter | Value min | Value Max | Unit | Source
HV line cost (230 KV) | 108000 | 152000 | USD/km | [2]
HV line cost (138 KV) | 44000 | 78000 | USD/km | [2]
HV line cost (69 KV) | 28000 | 28000 | USD/km | [2]
MV line cost (33 kV) | 5000 | 9000 | USD/km | [3]
LV line cost (0.2 kV) | 3500 | 5000 | USD/km | [3]
Transformers | 5000 | 5000 | USD/50 kVA | [3]
Additional Connection cost per household connected to grid | 125 | 125 | USD/HH | [3],[8]
Additional Connection cost per household connected with microgrid | 100 | 100 | USD/HH | [3],[8]
Distribution losses | 12% | 12% |  | [3]
O&M costs of distribution | 2% | 2% | Of Capital Cost/year | [3]
Main assumptions (additional to the costs listed below):
HV grid expansion is consistent with the African Development Bank’s plan [12], and with the extensions to planned power plants and those under construction [13]. Finally HV lines to mining locations far from the power grid are assumed to be built in the study (in cases where it would have been economically infeasible to connect them through an extension of MV lines).
A so-called buffer zone is set around the network in order to reach the current access to electricity rate (ca. 45%) (equivalent to around 19.6 % of the total area of Nigeria). It is assumed that settlements within this zone are connected to the power grid. For the settlements outside this zone, an analysis based on the distance from the closest connected point, population and resource availability indicates the optimal grid/micro grid/stand-alone solution.
Outside of these areas, three electrification options are investigated based on their LCOE: (1) an extension of the MV grid, (2) micro grid solutions, and (3) stand-alone systems. This analysis is performed for each 2.5 x 2.5 km2 cell drawing on GIS tools.
For consecutive MV grid extensions, a strengthening cost component is added to the previous extension. This additional cost is set at 10% of the capital cost expenditure required to reach the point at which the new line is being added. The maximum extension of MV lines is limited to 50 km.
The length of MV and LV lines for electricity distribution within an area are calculated according to the methodology described in the following paper: ‘Model-based scenarios for rural electrification in developing countries Bas J. van Ruijven, Jules Schers, Detlef P. van Vuuren (Energy, 2012)’
For micro-grids it is assumed that:
– No MV lines are necessary
– The length of LV lines is 3/4 the one that would be required for a grid extension in the same area.

## References
References
Ref. Number | Acronym | Full reference
1 | WB-ESMAP META | Model for Electricity Technology Assessments (META); 2012
2 | ESMAP-A | Model for Electricity Technology Assessments (META); annexes, 2006
3 | ESMAP | Technical and Economic Assessment of Off-grid, Mini-grid and Grid Electrification Technologies ; ESMAP Technical Paper 121/07
4 | WB - indicators | http://data.worldbank.org/country/nigeria
5 | IRENA | Renewable Power Generation Costs in 2012: An Overview
6 | InfoResources | FOCUS No 2/06 , Sustainable Energy; Rural Energy Poverty Alleviation
7 | IEA-WEO 2011 | IEA - World Energy Outlook 2011
8 | Columbia | Liberia Power Sector Capacity Building and Energy Master Planning; Modi Research Group, Energy Planning Team; August 2013
9 | WB Data | http://data.worldbank.org/indicator
10 | Energy, 2012 | ‘Model-based scenarios for rural electrification in developing countries Bas J. van Ruijven, Jules Schers, Detlef P. van Vuuren (Energy, 2012)’
11 | Renewable and Sustainable Energy Reviews, 2013 | S. Szabó et. al., Sustainable energy planning: Leapfrogging the energy poverty gap in Africa, Renewable and Sustainable Energy Reviews, 2013
12 | AFdB | African Development Bank Group; 2011 Africa Infrastructure Knowledge Program
13 | InfrastructureAfrica | http://www.infrastructureafrica.org/library/doc/773/nigeria-electricity-transmission-lines-data ; http://www.infrastructureafrica.org/library/doc/774/nigeria-power-plants-data
14 | Small Hydro potentials | UNIDo, World Small Hydropower Development Report, 2013
Maps
Ref. Number | Acronym | Full reference
a
b
c
d
e
f
g
h
i
l
m
n
o

## Sens. analyses
Sensitivity analyses undertaken:
1) Varying access targets for Nigeria
- Used for the WEO R: 170; U: 350
For sensitivity, varied:
- R: 130; 150; 190
2) Varying (grid?) Costs: